## Slide 1: 2Wire Decoder Types DC vs. AC
By Tony Ware B.Sc.
2-Wire Systems Specialist
Tonick Watering; a division of Aquamonix Pty Ltd
Notes: <number>
This section highlights the differences between 2Wire decoder types.
As with all engineering techniques, that which brings great advantages has disadvantages in other areas. This section allows the student to distinguish between the types and evaluate which will be best for a particular project.

## Slide 2: Solenoid Power Reduction The key to getting distance and many on together
Remember the fridge door? A good pull is required to part the magnet in the fridge from the one in the door when they are close together. Once they are pulled apart, even a little way, the force decreases dramatically.
If DC is applied to pull the solenoid plunger, because the force is much greater once it is fully retracted, the amount of DC can be reduced to quite small values before the spring overcomes the attraction and pulls the plunger out again.
This is very useful if you want lots of solenoids energized on the same wire, or long distances, because if the holding power is reduced there is more to go round for others to be turned on. Note that full power is required to start the pull, it can only be reduced once the solenoid plunger is fully pulled in.
This system does not work with AC on the solenoid because the attractive force varies during the cycle and falls to zero twice each cycle as the AC volts go through zero on their way to the opposite polarity.
NOTE: Even if the system uses DC on the solenoid, the main 2Wire path is always AC in some form.
Notes: <number>
DC on an AC solenoid?
Yes, all AC solenoids work well with DC. Less current is needed than with AC because AC attractive force varies during the cycle and falls to zero twice each cycle as the AC volts go through zero on their way to the opposite polarity.
HANDY TIP. Finding which valve is operated with which solenoid.
Take the battery out of your electric drill. Touch the solenoid leads (disconnected from the decoder!) to the battery terminals. This will operate the solenoid and you can see where the water is coming out.

## Slide 3: DC on the solenoid. Engineering disadvantages
Note however that the engineering advantage gained by this clever technique can bring its own problems.
DC on field wiring causes electrolytic destruction if exposed copper wires come into contact with wet soil. Good cable and joint insulation is mandatory.
The controller has to apply the full DC power for the correct amount of time to make sure the plunger is fully in before reducing the DC voltage. Controllers which use this technique have to be ‘tuned’ to the make of solenoid fitted.
Because of potentially destructive electrolytic action caused by field cable leakage to the earth, controllers which employ this technique may refuse to irrigate if they detect leakage. It must be located and rectified before watering can continue.

## Slide 4: Comparison of maximum wire length of Pure AC vs. DC on solenoid decoders
Maximum Wire length DC on Solenoid vs. Pure AC System |  |  |  |  | 
Nominal wire size | Ohms per 1000’ or Ohms per Km, per conductor | Rain Bird ESP-LXD, DC on solenoid | Rain Bird ESP-LXD, DC on solenoid | Underhill Sapien, Pure AC system | Underhill Sapien, Pure AC system
 |  | Max 8 stations on together | Max 8 stations on together | Max 4 stations on together | Max 4 stations on together
 |  | STAR | LOOP | STAR | LOOP
2.5mm2 | 7.5 Ohms/Km | 3.0Km | 12.0 Km | 1.6Km | 3.2Km
14 AWG | 2.58 Ohms/1000’ | 1.65 miles | 6.61 Miles | 0.88 Miles | 1.77 Miles
Note: All examples here using Rain Bird Solenoids. Pure AC systems can go further with some other solenoid types |  |  |  |  | 
ESP-LXD puts 10VAC with a 4.78VDC component on a held solenoid |  |  |  |  | 
Pure AC distances calculated on 4 solenoids clustered together. Better distances possible when distributed along path. |  |  |  |  | 
Notes: <number>
Note the significantly better distance with the ESP-LXD compared with the Sapien.
Both examples here have performance that are typical of their type.
When pure AC is to be considered, the solenoid type must be carefully chosen. When read with ‘WireMaxRunsPureACnotes.pdf’, the spreadsheet ‘WireMaxRunsPureAC1.xls’ will allow the student to evaluate the use of a particular solenoid.
When a DC on the solenoid system is used, this dependence on the solenoid type is greatly reduced and the user can be assured of much greater distances or more solenoids on together.

## Slide 5: Maximum Cable Distance for Various Types
DC on the solenoid ( or latching) is a very effective technique. It is the only way to get a significant number of solenoids on together over a large distance.
The distances obtainable depend on the number of solenoids on together, the cable size (AWG), the make of solenoids used and loop or branch cable routing.
Consult the manufacturer’s installation instructions for these figures.
Pure AC systems have much less obtainable distance than DC or latching. The type of solenoid is also critical, distances can be drastically different from one to another.
The spreadsheet MaxWireRunsPureAC.xls and the notes accompanying it can be used to determine maximum distances obtainable for Pure AC. This spreadsheet is usable for all Pure AC types.
Notes: <number>
Please distribute MaxWireRunsPureAC1.xls and MaxWireRunsPureACNotes.doc

## Slide 6: Identifying Pure AC and DC on the solenoid
A multi-wire system is Pure AC.
If the decoder system manufacturer states that more than 4 solenoids may active at a time, the system probably uses DC.
DC on the solenoid ( or latching) is a very effective technique and in no way inferior to Pure AC. It is the only way to get a significant number of solenoids on together over a large distance.
It does however preclude retrofit in most cases
DC on the Solenoid adds to the projects costs compared to Pure AC.
Manufacturers usually do not explicitly state DC is used, instead they specify that new wire and top quality wire joiners must be used. This ensures there will be no cable leakage to ground.
Notes: <number>
The increase in project costs with DC on the solenoid must be recognized. This is quantified in the spreadsheet ‘LandscapeProjectCostingExample.xls’ and its notes ‘LandscapeProjectCostingExample1-3.pdf’
This same spreadsheet allows the student to compare the differential project costs between multi-wire, DC on the solenoid and pure AC decoder systems.

## Slide 7: Toro TDC Decoder System with Latching Solenoids
The maximum allowable comm wire run from the Gateway to the furthest decoder using 2,5mm2 wire is 4,5km.
The station decoder modules are available in 1-, 2-, and 4-station configurations.
The decoder modules are connected to the Gateway via two-wire communication cable.
For PC-controlled systems, the maximum station capacity per output board is 800 stations.
The maximum number of decoders per wire path is 250, however these decoders may have 1, 2 or 4 station outputs, and no more than 500 decoders are run from any one output board.
A maximum of 1000 decoders can operated by a Gateway when equipped with two output boards and four communication cable wire paths.
This allows for the capacity of 1600 stations, however it should be achieved over four separate two-wire paths and would require the use of multi-station decoders.
Notes: <number>
This system is different from the others we have talked about.
Worth considering for very large PC driven systems with many decoders needed on at the same time. Primarily aimed at the golf, ‘wall-to-wall’ watering market.

## Slide 8: Toro TDC Latching Solenoid Decoder System

## Slide 9: DC or Pure AC? Which to choose.
Long distances and/or many on together? Must use DC on solenoid or latching solenoid TDC
Very long distances, where wire costs dominate? Must use DC on solenoid or latching solenoid TDC
Only 1 - 4 stations on together and medium distances? DC or AC will do*.
Re-use old wiring; retrofit? Best use Pure AC.
Hybrid system: Re-use two existing valve wires as the 2 wire path to expand stations without having to trench back to the controller? Best use Pure AC.
*Pure AC usually results in lower project cost, if it meets the performance requirements.
Notes: <number>
If you are looking at a new project that with multi-wire, would require satellites, then a DC on solenoid system will be best.
If you are looking to retrofit a satellite system to 2wire and want to use the old wiring and satellite positions, a Pure AC system will give less trouble.